## HSC-AD
SMARTEMP PRODUCT SELECTION CALCULATOR
Adjustable Helical Swirl Diffuser [HSC-AD]
Project: | <Project Name>
Inputs | [6 empty] | Optional | [12 empty] | v 5.4 [08/19]
| Diffuser Airflow Rate | 600 |  | [L/s] | [m3/h] |  |  | ADPI ≥ | 90% |  | default ≥ 90%
|  | = 2160 | m³/h
| Turndown to | 100 | % |  |  |  | Draught Rating & Heating
| Maximum Static Pressure | 60 | Pa | default 60 Pa |  |  | Diffuser Distance = Average(Max, Min) Centreline Distance
[7 empty] | OR |  | nominal distance = 10.1 | m | see rows 47 and 48
| Diffuser Height | 6 | m | 2 m ≤ height ≤ 20 m |  |  | Manual Diffuser Distance |  | 11.7 | m | centreline distance between diffusers
[7 empty] | OR |  | = specific airflow rate: 5.9 | L/s/m²
| ΔT (cooling) | -12 | K | 0 K to -15 K (default -12 K) |  |  | Specific Airflow Rate |  | 10 | L/s/m² | ≤ 30 L/s/m²
[9 empty] | average diffuser centreline distance: 10.1 | m
[8 empty] | Diffuser Location |  | Closed Ceiling | Freely Suspended (≥ 600mm below ceiling)
[8 empty] | ΔT (heating) | 4 | K | check for manual input
[8 empty] | Room Temperature (cooling) | 23 | °C | 20 °C to 26 °C
[8 empty] | Room Temperature (heating) | 20 | °C | check for manual input
[9 empty] | auto room temp. (heating) = 21 | °C
[8 empty] | Room Temp. @ heating startup | 16 | °C | night setback temperature
[8 empty] | % Low Level Return (heating) | 0% |  | 0% to 100% (default 0%)
Thermal Comfort Guide
[8 empty] | ADPI ≥ 95%; ṽ ≤ 0.20 m/s: | Premium comfort, sedentary activity, such as in auditoria.
[8 empty] | ADPI ≥ 90%; ṽ ≤ 0.25 m/s: | High comfort near-sedentary activity, such as in board rooms, high end offices and libraries.
[8 empty] | ADPI ≥ 80%; ṽ ≤ 0.29 m/s: | Good comfort near sedentary activity, such as open-plan offices and meeting rooms.
[8 empty] | ADPI ≥ 70%; ṽ ≤ 0.33 m/s: | Standard comfort medium activity, such as in transient spaces, retail and lobbies.
[11 empty] | not available in all regions |  | FUSION DN1340 |  |  |  | Key: | Suitable | Not Suitable | Warning
|  |  | DN250-R1 | DN250-R0 | DN355-R1 | DN355-R0 | DN500-R1 | DN500-R0 | DN710-R1 | DN710-R0 | DN1000-R1 | DN1000-R0 |  |  |  |  | Note: | R0 - no reducer; R1 - with reducer
Max Airflow [L/s] |  |  | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 |  |  |  | Note: | Max operating temperature 50°C
Max Permissible Airflow [L/s] |  |  | 178.5576 | 199.371 | 358.2106 | 451.3234 | 660.5534 | 779.9569 | 1331.9399 | 1572.7051 | 2642.2136 | 3119.8277 | 5601.9626
Min Airflow (Turndown To) [L/s] |  |  | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
Min Permissible Airflow [L/s] |  |  | 59.1 | 84.4 | 118.9 | 169.6 | 234.6 | 335 | 471.8 | 672.6 | 930.7 | 1328.8 | 2385.9933
Static Pressure @ Airflow Rate [Pa] |  |  | 585.9712 | 451.9026 | 145.8291 | 83.5352 | 43.7843 | 29.7875 | 10.7688 | 7.3262 | < 5 | < 5 | < 5
Total Pressure @ Airflow Rate [Pa] |  |  | 677.4813 | 543.4126 | 168.336 | 106.042 | 49.5037 | 35.5069 | 12.1754 | < 10 | < 10 | < 10 | < 10
Max Permissible Static Pressure [Pa] |  |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Sound Power Level [dB(A)] |  |  | 86.1895 | 81.5751 | 70.3388 | 61.193 | 51.333 | 45.9814 | 32.9475 | 29.0703 | < 20 | < 20 | < 20
Max Recommended ΔT (heating) [K] |  |  | 81.0065 | 56.7963 | 28.2286 | 19.836 | 10.1258 | 7.0995 | 3.5286 | 2.4795 | 1.2612 | < +1 K | < +1 K | Warning: Maximum Permissible ΔT < Selected ΔT (heating) when guide ring is fully down
Room Temp. @ heating startup [°C] |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | - | * | 'Guide Ring Position' @ max ΔT is the distance from diffuser face to guide ring trailing edge
Max Recommended Centreline Dist. [m] |  |  | - | 44.5 | 19.6 | 17.2 | 15.5 | 14.9 | 13.6 | 13.4 | 13 | 12.9 | 12.7
Min Recommended Centreline Dist. [m] |  |  | - | 31.2 | 7 | 6.3 | 5.7 | 5.5 | 5.1 | 5.1 | 4.9 | 4.9 | 4.8
Min Recommended Diffuser Height [m] |  |  | 2.8 | 2.8 | 2.8 | 3.3 | 3.9 | 4.4 | 5 | 5.5 | 6.1 | 6.6 | 7.2
Mean Room Air Velocity [m/s] |  |  |  | 0.19567 | 0.16851 | 0.16051 | 0.15187 | 0.14797 | 0.13747 | 0.13544 | 0.13078 | 0.1297 | 0.127 | Note: | Comfort criteria valid for diffuser spacing of 10.1 m & room temperature of 23 °C
Mean Draught Rating (DR) |  |  |  | 20.11% | 16.52% | 15.48% | 14.38% | 13.89% | 12.57% | 12.31% | 11.73% | 11.6% | 11.26% |  | see cells L14 & L23
Mean PPD |  |  |  | 10.05% | 8.493% | 8.07% | 7.629% | 7.436% | 6.931% | 6.837% | 6.621% | 6.572% | 6.45%
Satifies PPD Category (ISO7730) |  |  |  | C | B | B | B | B | B | B | B | B | B
¦PMV¦ (ISO7730; ASHRAE Std 55) |  |  |  | 0.5126 | 0.42348 | 0.39426 | 0.3608 | 0.34496 | 0.29972 | 0.29054 | 0.26865 | 0.26344 | 25.02%
Thermal Element Setting [°C] |  |  | n.r. | n.r. | n.r. | n.r. | 30 | 26 | 24 | 22 | 22 | 22 | - | Note: 'n.r.' - thermal element not recommended
Product Code & Control Voltage Generator
Select Size & Reducer
|  |  | DN250-R1 | DN250-R0 | DN355-R1 | DN355-R0 | DN500-R1 | DN500-R0 | DN710-R1 | DN710-R0 | DN1000-R1 | DN1000-R0
Face Shape |  |  | C750* | S595 | S603 | custom | N/A
Adjustment Type |  |  | Manual* |  | Electric motor 2-10V |  | Electric motor 2-position |  | Thermal actuator set to 26°C
Colour |  |  | RAL9003* (signal white) |  | RAL9005 (jet black) |  | other^
|  | Order Code | SMARTEMP HSC-AD-DN500-R0-C750-M-RAL9003 |  |  |  |  | * indicates standard/default option
|  | Product Description |  | • Diffuser HSC-AD-DN500-R0 (neck diameter 500 mm without reducer) |  |  |  | ^ contact Smartair Diffusion for custom colours
• 750 mm diameter circular face
• Manual adjustment
|  |  |  | • Powder coated to RAL9003 (signal white) |  |  |  | refer to 'HSC-AD Selection Summary' for a printable summary
[6 empty] | click to see product on smartair.asia | [9 empty] | Copyright © 2019 SMARTAIR DIFFUSION
Group Box 8
Group Box 45
Group Box 52
Group Box 109
Horizontal Discharge
Vertical Discharge
Group Box 347
Group Box 607

## Equations HSC-AD (hidden)
Units
| Unit Type | 1 | [L/s] | L/s |  | L/s/m²
| Multiplier | 1
| Alternate | 3.6 | m³/h
Input
Size
| Max airflow rate | 600
| Turndown to | 1
| min flowrate | 600
| max pressure | 60
| diffuser height | 6
| dT cooling | 12
| Tn.s. | 16
| adpi | 90%
| Mean room v | 0.25
| Room Temp Cooling | 23 | C
| room temp checkbox | FALSE
| Room Temp Heating | 21
| T max Correction | 4 | K
| dT heating checkbox | FALSE
| dT heating manual input | 4 | K
| adjusted heating height | 6
Hmin
| adpi |  |  | Hmin factor | Factor
| 70% | 0 | 0.2 | 0.9 | 110%
| 80% | 2 |  | 1
| 90% | 4 |  | 1.1
| 95% | 5 |  | 1.15
| Freely Suspended | 2 | free
| Cmin Multiplier | 0.85
| Cmax Multiplier | 0.8
| Cmin | x = velocity
| H | ax | ^b | Q''
| 2.7 | 4510 | 2.2693 | 194.0536
| 4 | 3884 | 2.2426 | 173.4201
| 10 | 3435 | 2.2754 | 146.5546
| 30 | 2736 | 2.2624 | 118.849
|  | Ax | ^b | Q'' Target
| 6 | 232.5287 | -0.1988 | 162.8476
| v' at Vmax | 13.5706
| v' at Vmin | 17.5706
| correction v' factor | 4
Cmax
| adpi | v' @Vmax | v' @ Vmin |  | Hfactor @ Vmax | Hfactor @ Vmin
| 95% | 0.955 | 1.27 |  | 5.317 | 4.4309
| 90% | 0.75 | 1 |  | 6 | 5
| 80% | 0.5 | 0.66 |  | 7.3659 | 6.1383
| 70% | 0.35 | 0.47 |  | 8.7318 | 7.2765
| v' & Vmax | 0.75 |  | at ADPI | 6 | factor * room height
| v' & Vmin | 1 |  |  | 5
| Diffuser Distance Selection Type | 1
| Manual Diffuser Distance | 11.7
| Specific Flow rate | 10 | max | 31
| dist spec flow rate | 7.746
heating factor
| Low level return | 0% | 1
| Penetration Constant | 4.642
| DN250 |  |  | pressure | v | [5 empty] | DN355 | [9 empty] | DN500 | [5 empty] | DN710 | [5 empty] | DN1000 | [5 empty] | DN1340
| Pressure at airflow | 543.4126 | p-v | 50 | 182 | 0.46374 |  |  |  |  | Pressure at airflow | 106.042 | p-v | 50 | 412 | 0.41165 |  |  |  |  | Pressure at airflow | 35.5069 | p-v | 50 | 712 |  | Pressure at airflow | 8.7329 | p-v | 50 | 1435.6768 |  | Pressure at airflow | 2.2192 | p-v | 50 | 2848 |  | Pressure at airflow | 0.68829 | p-v | 50 | 5113.8688
| Neck Dia. | 250 | [8 empty] | Neck Dia. | 355 | [8 empty] | Neck Dia. | 500 |  | 42.9633 | 660 |  | Neck Dia. | 710 |  |  |  |  | Neck Dia. | 1000 |  |  |  |  | Neck Dia. | 1340
| Neck Area | 0.049087 | [8 empty] | Neck Area | 0.09898 | [8 empty] | Neck Area | 0.19635 |  |  |  | 770 | Neck Area | 0.39592 |  |  |  |  | Neck Area | 0.7854 |  |  |  |  | Neck Area | 1.4103
| Static Pressure | 451.9026 | [8 empty] | Static Pressure | 83.5352 | [8 empty] | Static Pressure | 29.7875 |  |  |  |  | Static Pressure | 7.3262 |  |  |  |  | Static Pressure | 1.8617 |  |  |  |  | Static Pressure | 0.57742
| Flow at max pressure | 199.371 | [8 empty] | Flow at max pressure | 451.3234 | [8 empty] | Flow at max pressure | 779.9569 |  |  |  |  | Flow at max pressure | 1572.7051 |  |  |  |  | Flow at max pressure | 3119.8277 |  |  |  |  | Flow at max pressure | 5601.9626
| Vmin | 84.4 | V at -12K | 84.4 | 12 | [5 empty] | Vmin | 169.6 | V at -12K | 169.6 | 12 | [5 empty] | Vmin | 335 | V at -12K | 335 | 12 |  | Vmin | 672.6 | V at -12K | 672.6 | 12 |  | Vmin | 1328.8 | V at -12K | 1328.8 | 12 |  | Vmin | 2385.9933 | V at -12K | 2385.9933 | 12
| SWL | 81.5751 |  | 14.05 | -6.91 | [5 empty] | SWL | 61.193 |  | 14.24 | -5.22 | [5 empty] | SWL | 45.9814 |  | 14.29 | -5.03 |  | SWL | 29.0703 |  | 14.33 | -1.9842 |  | SWL | 12.4845 |  | 14.33 | 1.0615 |  | SWL | -2.1255 |  | 14.33 | 3.2273
| Diameter | 250 | [8 empty] | Diameter | 355 | [8 empty] | Diameter | 500 |  |  |  |  | Diameter | 710 |  |  |  |  | Diameter | 1000 |  |  |  |  | Diameter | 1340
| Area | 0.049087 | [8 empty] | Area | 0.09898 | [8 empty] | Area | 0.19635 |  |  |  |  | Area | 0.39592 |  |  |  |  | Area | 0.7854 |  |  |  |  | Area | 1.4103
| velocity | 12.2231 | [8 empty] | velocity | 6.0618 | [8 empty] | velocity | 3.0558 |  |  |  |  | velocity | 1.5155 |  |  |  |  | velocity | 0.76394 |  |  |  |  | velocity | 0.42545
| Heating | [9 empty] | Heating | [9 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating
| dT Heating | 56.7963 | [8 empty] | dT Heating | 19.836 | [8 empty] | dT Heating | 7.0995 |  |  |  |  | dT Heating | 2.4795 |  |  |  |  | dT Heating | 0.88744 |  |  |  |  | dT Heating | 0.36883 | H |  |  |  | K
| dT Heating low level corrected | 56.7963 | [8 empty] | dT Heating low level corrected | 19.836 | [8 empty] | dT Heating low level corrected | 7.0995 |  |  |  |  | dT Heating low level corrected | 2.4795 |  |  |  |  | dT Heating low level corrected | 0.88744 |  |  |  |  | dT Heating low level corrected | 0.36883 | 6 | 4.43e-05 | 1.673 |  | 1.969
| dT Heating | 56.7963 | [8 empty] | dT Heating | 19.836 | [8 empty] | dT Heating | 7.0995 |  |  |  |  | dT Heating | 2.4795 |  |  |  |  | dT Heating | 0.88744 |  |  |  |  | dT Heating | 0.36883
| dT corrected thermal element | 60.7963 | [8 empty] | dT corrected thermal element | 23.836 | [8 empty] | dT corrected thermal element | 11.0995 |  |  |  |  | dT corrected thermal element | 6.4795 |  |  |  |  | dT corrected thermal element | 4.8874 |  |  |  |  | dT corrected thermal element | 4.3688
| T s. | 76.7963 | [8 empty] | T s. | 39.836 | [8 empty] | T s. | 27.0995 |  |  |  |  | T s. | 22.4795 |  |  |  |  | T s. | 20.8874 |  |  |  |  | T s. | 20.3688
| T element setting | n.r. | [8 empty] | T element setting | n.r. | [8 empty] | T element setting | 26 |  |  |  |  | T element setting | 22 |  |  |  |  | T element setting | 22 |  |  |  |  | T element setting | 22
| Min Height | [9 empty] | Min Height | [9 empty] | Min Height | [5 empty] | Min Height | [5 empty] | Min Height | [5 empty] | Min Height
| Hmin | 2.5 | [8 empty] | Hmin | 3 | [8 empty] | Hmin | 4 |  |  |  |  | Hmin | 5 |  |  |  |  | Hmin | 6 |  |  |  |  | Hmin | 6.5
| Hmin Factor | 2.75 | [8 empty] | Hmin Factor | 3.3 | [8 empty] | Hmin Factor | 4.4 |  |  |  |  | Hmin Factor | 5.5 |  |  |  |  | Hmin Factor | 6.6 |  |  |  |  | Hmin Factor | 7.15
| Distance Selection | [9 empty] | Distance Selection | [9 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection
| Vmax | 182 | [8 empty] | Vmax | 412 | [8 empty] | Vmax | 660 |  |  |  |  | Vmax | 1435.6768 |  |  |  |  | Vmax | 2848 |  |  |  |  | Vmax | 5113.8688
| Vmin | 54.6 | [8 empty] | Vmin | 123.6 | [8 empty] | Vmin | 198 |  |  |  |  | Vmin | 430.703 |  |  |  |  | Vmin | 854.4 |  |  |  |  | Vmin | 1534.1606
| Cmin | [9 empty] | Cmin | [9 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin
| v' | 0.44662 | [8 empty] | v' | 10.9631 | [8 empty] | v' | 14.0901 |  |  |  |  | v' | 16.8968 |  |  |  |  | v' | 18.0811 |  |  |  |  | v' | 18.6145
| Cmin | 36.6528 | [8 empty] | Cmin | 7.3979 | [8 empty] | Cmin | 6.5256 |  |  |  |  | Cmin | 5.959 |  |  |  |  | Cmin | 5.7605 |  |  |  |  | Cmin | 5.6774
| Cmin Freely Suspended | 31.1549 | adjusts for adpi/temp/height through Q vs u_max | [7 empty] | Cmin Freely Suspended | 6.2882 | adjusts for adpi/temp/height through Q vs u_max | [7 empty] | Cmin Freely Suspended | 5.5467 | adjusts for adpi/temp/height through Q vs u_max |  |  |  | Cmin Freely Suspended | 5.0651 | adjusts for adpi/temp/height through Q vs u_max |  |  |  | Cmin Freely Suspended | 4.8965 | adjusts for adpi/temp/height through Q vs u_max |  |  |  | Cmin Freely Suspended | 4.8258 | adjusts for adpi/temp/height through Q vs u_max
| Cmax | [9 empty] | Cmax | [9 empty] | Cmax | [5 empty] | Cmax | [5 empty] | Cmax | [5 empty] | Cmax
| v' @ V | -0.070251 | [8 empty] | v' @ V | 0.58703 | [8 empty] | v' @ V | 0.78247 |  |  |  |  | v' @ V | 0.95789 |  |  |  |  | v' @ V | 1.0319 |  |  |  |  | v' @ V | 1.0652
| H Factor | 9.281 | [8 empty] | H Factor | 6.6519 | [8 empty] | H Factor | 5.8701 |  |  |  |  | H Factor | 5.1685 |  |  |  |  | H Factor | 4.8724 |  |  |  |  | H Factor | 4.739
| c max eqn | #NUM! | [8 empty] | c max eqn | 21.4462 | [8 empty] | c max eqn | 18.5759 |  |  |  |  | c max eqn | 16.789 |  |  |  |  | c max eqn | 16.1757 |  |  |  |  | c max eqn | 15.9206
| c max room height | 55.686 | [8 empty] | c max room height | 39.9112 | [8 empty] | c max room height | 35.2208 |  |  |  |  | c max room height | 31.0108 |  |  |  |  | c max room height | 29.2343 |  |  |  |  | c max room height | 28.4342
| Cmax | 44.5488 | [8 empty] | Cmax | 17.157 | [8 empty] | Cmax | 14.8607 |  |  |  |  | Cmax | 13.4312 |  |  |  |  | Cmax | 12.9405 |  |  |  |  | Cmax | 12.7364
| Spacing | [9 empty] | Spacing | [9 empty] | Spacing | [5 empty] | Spacing | [5 empty] | Spacing | [5 empty] | Spacing
| Avg Diffuser Distance | 10.0593 | [8 empty] | Avg Diffuser Distance | 10.0593 | [8 empty] | Avg Diffuser Distance | 10.0593 |  |  |  |  | Avg Diffuser Distance | 10.0593 |  |  |  |  | Avg Diffuser Distance | 10.0593 |  |  |  |  | Avg Diffuser Distance | 10.0593
| Dist. From Spec. flowrate | 7.746 | [8 empty] | Dist. From Spec. flowrate | 7.746 | [8 empty] | Dist. From Spec. flowrate | 7.746 |  |  |  |  | Dist. From Spec. flowrate | 7.746 |  |  |  |  | Dist. From Spec. flowrate | 7.746 |  |  |  |  | Dist. From Spec. flowrate | 7.746
| Distance Selected | 10.0593 | [8 empty] | Distance Selected | 10.0593 | [8 empty] | Distance Selected | 10.0593 |  |  |  |  | Distance Selected | 10.0593 |  |  |  |  | Distance Selected | 10.0593 |  |  |  |  | Distance Selected | 10.0593
| Area | 101.1894 | [8 empty] | Area | 101.1894 | [8 empty] | Area | 101.1894 |  |  |  |  | Area | 101.1894 |  |  |  |  | Area | 101.1894 |  |  |  |  | Area | 101.1894
| V" | 5.9295 | [8 empty] | V" | 5.9295 | [8 empty] | V" | 5.9295 |  |  |  |  | V" | 5.9295 |  |  |  |  | V" | 5.9295 |  |  |  |  | V" | 5.9295
| Q" | 71.1537 | W/m2 | note: Q*1.2 density ignored to compensate for mean velocity to max velocity | [6 empty] | Q" | 71.1537 | W/m2 | note: Q*1.2 density ignored to compensate for mean velocity to max velocity | [6 empty] | Q" | 71.1537 | W/m2 | note: Q*1.2 density ignored to compensate for mean velocity to max velocity |  |  | Q" | 71.1537 | W/m2 | note: Q*1.2 density ignored to compensate for mean velocity to max velocity |  |  | Q" | 71.1537 | W/m2 | note: Q*1.2 density ignored to compensate for mean velocity to max velocity |  |  | Q" | 71.1537 | W/m2 | note: Q*1.2 density ignored to compensate for mean velocity to max velocity
| V'' correction factor | -4.8637 | [8 empty] | V'' correction factor | -0.96631 | [8 empty] | V'' correction factor | 0.19252 |  |  |  |  | V'' correction factor | 1.2326 |  |  |  |  | V'' correction factor | 1.6715 |  |  |  |  | V'' correction factor | 1.8692
| V'' corrected | 10.7931 | [8 empty] | V'' corrected | 6.8958 | [8 empty] | V'' corrected | 5.737 |  |  |  |  | V'' corrected | 4.6968 |  |  |  |  | V'' corrected | 4.2579 |  |  |  |  | V'' corrected | 4.0603
| Q'' adjusted | 93.5764 | [8 empty] | Q'' adjusted | 59.7865 | [8 empty] | Q'' adjusted | 49.7394 |  |  |  |  | Q'' adjusted | 40.7214 |  |  |  |  | Q'' adjusted | 36.9164 |  |  |  |  | Q'' adjusted | 35.2025
| V | 2.7 | 0.024532 | 0.44066 | 0.18128 | [5 empty] | V | 2.7 | 0.024532 | 0.44066 | 0.1488 | [5 empty] | V | 2.7 | 0.024532 | 0.44066 | 0.13721 |  | V | 2.7 | 0.024532 | 0.44066 | 0.12564 |  | V | 2.7 | 0.024532 | 0.44066 | 0.12032 |  | V | 2.7 | 0.024532 | 0.44066 | 0.11783
|  | 4 | 0.02509 | 0.44591 | 0.18987 | [6 empty] | 4 | 0.02509 | 0.44591 | 0.15549 | [6 empty] | 4 | 0.02509 | 0.44591 | 0.14324 |  |  | 4 | 0.02509 | 0.44591 | 0.13102 |  |  | 4 | 0.02509 | 0.44591 | 0.12541 |  |  | 4 | 0.02509 | 0.44591 | 0.12278
|  | 10 | 0.027927 | 0.43948 | 0.20526 | [6 empty] | 10 | 0.027927 | 0.43948 | 0.16858 | [6 empty] | 10 | 0.027927 | 0.43948 | 0.15549 |  |  | 10 | 0.027927 | 0.43948 | 0.1424 |  |  | 10 | 0.027927 | 0.43948 | 0.13639 |  |  | 10 | 0.027927 | 0.43948 | 0.13357
|  | 30 | 0.030254 | 0.442 | 0.22493 | [6 empty] | 30 | 0.030254 | 0.442 | 0.18452 | [6 empty] | 30 | 0.030254 | 0.442 | 0.17011 |  |  | 30 | 0.030254 | 0.442 | 0.15571 |  |  | 30 | 0.030254 | 0.442 | 0.14911 |  |  | 30 | 0.030254 | 0.442 | 0.14601
| Room Height |  | Ax | ^b |  | m/s |  |  |  |  | Room Height |  | Ax | ^b |  | m/s |  |  |  |  | Room Height |  | Ax | ^b |  | m/s | Room Height |  | Ax | ^b |  | m/s | Room Height |  | Ax | ^b |  | m/s | Room Height |  | Ax | ^b |  | m/s
|  | 6 | 0.16709 | 0.088114 | 0.19567 | [6 empty] | 6 | 0.13701 | 0.08835 | 0.16051 | [6 empty] | 6 | 0.12628 | 0.088447 | 0.14797 |  |  | 6 | 0.11557 | 0.088552 | 0.13544 |  |  | 6 | 0.11066 | 0.088604 | 0.1297 |  |  | 6 | 0.10835 | 0.088629 | 0.127
| DR | 20.11% | [8 empty] | DR | 15.48% | [8 empty] | DR | 13.89% |  |  |  |  | DR | 12.31% |  |  |  |  | DR | 11.6% |  |  |  |  | DR | 11.26%
| PPD | 10.05% | [8 empty] | PPD | 8.07% | [8 empty] | PPD | 7.436% |  |  |  |  | PPD | 6.837% |  |  |  |  | PPD | 6.572% |  |  |  |  | PPD | 6.45%
| ISO category | C | [8 empty] | ISO category | B | [8 empty] | ISO category | B |  |  |  |  | ISO category | B |  |  |  |  | ISO category | B |  |  |  |  | ISO category | B
| PMV | 0.5126 | [8 empty] | PMV | 0.39426 | [8 empty] | PMV | 0.34496 |  |  |  |  | PMV | 0.29054 |  |  |  |  | PMV | 0.26344 |  |  |  |  | PMV | 0.25019
| V'' Result | 5.9295 | [8 empty] | V'' Result | 5.9295 | [8 empty] | V'' Result | 5.9295 |  |  |  |  | V'' Result | 5.9295 |  |  |  |  | V'' Result | 5.9295 |  |  |  |  | V'' Result | 5.9295
| Distance Result | 10.0593 | [8 empty] | Distance Result | 10.0593 | [8 empty] | Distance Result | 10.0593 |  |  |  |  | Distance Result | 10.0593 |  |  |  |  | Distance Result | 10.0593 |  |  |  |  | Distance Result | 10.0593
| R1 | [9 empty] | R1 | [9 empty] | R1 | [5 empty] | R1 | [5 empty] | R1
| Pressure at airflow | 677.4813 | p-v | 50 | 163 | [5 empty] | Pressure at airflow | 168.336 | p-v | 50 | 327 | [5 empty] | Pressure at airflow | 49.5037 | p-v | 50 | 603 |  | Pressure at airflow | 12.1754 | p-v | 50 | 1215.8892 |  | Pressure at airflow | 3.094 | p-v | 50 | 2412
| Neck Dia. | 250 | [8 empty] | Neck Dia. | 355 | [8 empty] | Neck Dia. | 500 |  | 42.9633 | 558.9607 |  | Neck Dia. | 710 |  |  |  |  | Neck Dia. | 1000
| Neck Area | 0.049087 | [8 empty] | Neck Area | 0.09898 | [8 empty] | Neck Area | 0.19635 |  |  |  |  | Neck Area | 0.39592 |  |  |  |  | Neck Area | 0.7854
| Static Pressure | 585.9712 | [8 empty] | Static Pressure | 145.8291 | [8 empty] | Static Pressure | 43.7843 |  |  |  |  | Static Pressure | 10.7688 |  |  |  |  | Static Pressure | 2.7365
| Flow at max pressure | 178.5576 | [8 empty] | Flow at max pressure | 358.2106 | [8 empty] | Flow at max pressure | 660.5534 |  |  |  |  | Flow at max pressure | 1331.9399 |  |  |  |  | Flow at max pressure | 2642.2136
| Vmin | 59.1 | V at -12K | 59.1 | 12 | [5 empty] | Vmin | 118.9 | V at -12K | 118.9 | 12 | [5 empty] | Vmin | 234.6 | V at -12K | 234.6 | 12 |  | Vmin | 471.8 | V at -12K | 471.8 | 12 |  | Vmin | 930.7 | V at -12K | 930.7 | 12
| SWL | 86.1895 |  | 14.39 | -7.61 | [5 empty] | SWL | 70.3388 |  | 15.63 | -9.78 | [5 empty] | SWL | 51.333 |  | 14.67 | -5.91 |  | SWL | 32.9475 |  | 14.328 | -2.8642 |  | SWL | 16.3667 |  | 14.33 | 0.18153
| Diameter | 209 | [8 empty] | Diameter | 297 | [8 empty] | Diameter | 418 |  |  |  |  | Diameter | 594 |  |  |  |  | Diameter | 837
| Area | 0.034307 | [8 empty] | Area | 0.069279 | [8 empty] | Area | 0.13723 |  |  |  |  | Area | 0.27712 |  |  |  |  | Area | 0.55023
| velocity | 17.4892 | [8 empty] | velocity | 8.6606 | [8 empty] | velocity | 4.3723 |  |  |  |  | velocity | 2.1652 |  |  |  |  | velocity | 1.0905
| Heating | [9 empty] | Heating | [9 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating
| dT Heating | 81.0065 | [8 empty] | dT Heating | 28.2286 | [8 empty] | dT Heating | 10.1258 |  |  |  |  | dT Heating | 3.5286 |  |  |  |  | dT Heating | 1.2612
| dT Heating low level corrected | 81.0065 | [8 empty] | dT Heating low level corrected | 28.2286 | [8 empty] | dT Heating low level corrected | 10.1258 |  |  |  |  | dT Heating low level corrected | 3.5286 |  |  |  |  | dT Heating low level corrected | 1.2612
| dT Heating | 81.0065 | [8 empty] | dT Heating | 28.2286 | [8 empty] | dT Heating | 10.1258 |  |  |  |  | dT Heating | 3.5286 |  |  |  |  | dT Heating | 1.2612
| dT corrected thermal element | 85.0065 | [8 empty] | dT corrected thermal element | 32.2286 | [8 empty] | dT corrected thermal element | 14.1258 |  |  |  |  | dT corrected thermal element | 7.5286 |  |  |  |  | dT corrected thermal element | 5.2612
| T s. | 101.0065 | [8 empty] | T s. | 48.2286 | [8 empty] | T s. | 30.1258 |  |  |  |  | T s. | 23.5286 |  |  |  |  | T s. | 21.2612
| T element setting | n.r. | [8 empty] | T element setting | n.r. | [8 empty] | T element setting | 30 |  |  |  |  | T element setting | 23.5286 |  |  |  |  | T element setting | 22
| Min Height | [9 empty] | Min Height | [9 empty] | Min Height | [5 empty] | Min Height | [5 empty] | Min Height
| Hmin | 2.5 | [8 empty] | Hmin | 2.5 | [8 empty] | Hmin | 3.5 |  |  |  |  | Hmin | 4.5 |  |  |  |  | Hmin | 5.5
| Hmin Factor | 2.75 | [8 empty] | Hmin Factor | 2.75 | [8 empty] | Hmin Factor | 3.85 |  |  |  |  | Hmin Factor | 4.95 |  |  |  |  | Hmin Factor | 6.05
| Distance Selection | [9 empty] | Distance Selection | [9 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection
| Vmax | 163 | [8 empty] | Vmax | 327 | [8 empty] | Vmax | 558.9607 |  |  |  |  | Vmax | 1215.8892 |  |  |  |  | Vmax | 2412
| Vmin | 48.9 | [8 empty] | Vmin | 98.1 | [8 empty] | Vmin | 167.6882 |  |  |  |  | Vmin | 364.7668 |  |  |  |  | Vmin | 723.6
| Cmin | [9 empty] | Cmin | [9 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin
| v' | -1.7493 | [8 empty] | v' | 8.8 | [8 empty] | v' | 13.1511 |  |  |  |  | v' | 16.4651 |  |  |  |  | v' | 17.8635
| Cmin | #NUM! | [8 empty] | Cmin | 8.2572 | [8 empty] | Cmin | 6.7545 |  |  |  |  | Cmin | 6.0366 |  |  |  |  | Cmin | 5.7955
| Cmin Freely Suspended |  | adjusts for adpi/temp/height through Q vs u_max | [7 empty] | Cmin Freely Suspended | 7.0186 | adjusts for adpi/temp/height through Q vs u_max | [7 empty] | Cmin Freely Suspended | 5.7413 | adjusts for adpi/temp/height through Q vs u_max |  |  |  | Cmin Freely Suspended | 5.1311 | adjusts for adpi/temp/height through Q vs u_max |  |  |  | Cmin Freely Suspended | 4.9262 | adjusts for adpi/temp/height through Q vs u_max
| Cmax | [9 empty] | Cmax | [9 empty] | Cmax | [5 empty] | Cmax | [5 empty] | Cmax
| v' @ V | -0.20749 | [8 empty] | v' @ V | 0.45183 | [8 empty] | v' @ V | 0.72378 |  |  |  |  | v' @ V | 0.9309 |  |  |  |  | v' @ V | 1.0183
| H Factor | 9.83 | [8 empty] | H Factor | 7.1927 | [8 empty] | H Factor | 6.1049 |  |  |  |  | H Factor | 5.2764 |  |  |  |  | H Factor | 4.9268
| c max eqn | #NUM! | [8 empty] | c max eqn | 24.4451 | [8 empty] | c max eqn | 19.3143 |  |  |  |  | c max eqn | 17.0306 |  |  |  |  | c max eqn | 16.2833
| c max room height | 58.9798 | [8 empty] | c max room height | 43.156 | [8 empty] | c max room height | 36.6293 |  |  |  |  | c max room height | 31.6583 |  |  |  |  | c max room height | 29.5608
| Cmax | 47.1839 | final selection | [7 empty] | Cmax | 19.5561 | [8 empty] | Cmax | 15.4514 |  |  |  |  | Cmax | 13.6245 |  |  |  |  | Cmax | 13.0267
| Spacing | [9 empty] | Spacing | [9 empty] | Spacing | [5 empty] | Spacing | [5 empty] | Spacing
| Avg Diffuser Distance | 10.0593 | [8 empty] | Avg Diffuser Distance | 10.0593 | [8 empty] | Avg Diffuser Distance | 10.0593 |  |  |  |  | Avg Diffuser Distance | 10.0593 |  |  |  |  | Avg Diffuser Distance | 10.0593
| Dist. From Spec. flowrate | 7.746 | [8 empty] | Dist. From Spec. flowrate | 7.746 | [8 empty] | Dist. From Spec. flowrate | 7.746 |  |  |  |  | Dist. From Spec. flowrate | 7.746 |  |  |  |  | Dist. From Spec. flowrate | 7.746
| Distance Selected | 10.0593 | [8 empty] | Distance Selected | 10.0593 | [8 empty] | Distance Selected | 10.0593 |  |  |  |  | Distance Selected | 10.0593 |  |  |  |  | Distance Selected | 10.0593
| Area | 101.1894 | [8 empty] | Area | 101.1894 | [8 empty] | Area | 101.1894 |  |  |  |  | Area | 101.1894 |  |  |  |  | Area | 101.1894
| V" | 5.9295 | [8 empty] | V" | 5.9295 | [8 empty] | V" | 5.9295 |  |  |  |  | V" | 5.9295 |  |  |  |  | V" | 5.9295
| Q" | 71.1537 | W/m2 | note: Q*1.2 density ignored to compensate for mean velocity to max velocity | [6 empty] | Q" | 71.1537 | W/m2 | note: Q*1.2 density ignored to compensate for mean velocity to max velocity | [6 empty] | Q" | 71.1537 | W/m2 | note: Q*1.2 density ignored to compensate for mean velocity to max velocity |  |  | Q" | 71.1537 | W/m2 | note: Q*1.2 density ignored to compensate for mean velocity to max velocity |  |  | Q" | 71.1537 | W/m2 | note: Q*1.2 density ignored to compensate for mean velocity to max velocity
| V'' correction factor | -5.6774 | [8 empty] | V'' correction factor | -1.768 | [8 empty] | V'' correction factor | -0.15548 |  |  |  |  | V'' correction factor | 1.0727 |  |  |  |  | V'' correction factor | 1.5909
| V'' corrected | 11.6069 | [8 empty] | V'' corrected | 7.6974 | [8 empty] | V'' corrected | 6.085 |  |  |  |  | V'' corrected | 4.8568 |  |  |  |  | V'' corrected | 4.3386
| Q'' adjusted | 100.6318 | [8 empty] | Q'' adjusted | 66.7368 | [8 empty] | Q'' adjusted | 52.7565 |  |  |  |  | Q'' adjusted | 42.1085 |  |  |  |  | Q'' adjusted | 37.6155
| V | 2.7 | 0.024532 | 0.44066 | 0.18718 | [5 empty] | V | 2.7 | 0.024532 | 0.44066 | 0.15619 | [5 empty] | V | 2.7 | 0.024532 | 0.44066 | 0.14082 |  | V | 2.7 | 0.024532 | 0.44066 | 0.12751 |  | V | 2.7 | 0.024532 | 0.44066 | 0.12132
|  | 4 | 0.02509 | 0.44591 | 0.19613 | [6 empty] | 4 | 0.02509 | 0.44591 | 0.16331 | [6 empty] | 4 | 0.02509 | 0.44591 | 0.14706 |  |  | 4 | 0.02509 | 0.44591 | 0.13299 |  |  | 4 | 0.02509 | 0.44591 | 0.12647
|  | 10 | 0.027927 | 0.43948 | 0.21193 | [6 empty] | 10 | 0.027927 | 0.43948 | 0.17693 | [6 empty] | 10 | 0.027927 | 0.43948 | 0.15956 |  |  | 10 | 0.027927 | 0.43948 | 0.14451 |  |  | 10 | 0.027927 | 0.43948 | 0.13752
|  | 30 | 0.030254 | 0.442 | 0.23227 | [6 empty] | 30 | 0.030254 | 0.442 | 0.19371 | [6 empty] | 30 | 0.030254 | 0.442 | 0.17459 |  |  | 30 | 0.030254 | 0.442 | 0.15804 |  |  | 30 | 0.030254 | 0.442 | 0.15035
| Room Height |  | Ax | ^b |  | m/s |  |  |  |  | Room Height |  | Ax | ^b |  | m/s |  |  |  |  | Room Height |  | Ax | ^b |  | m/s | Room Height |  | Ax | ^b |  | m/s | Room Height |  | Ax | ^b |  | m/s
|  | 6 | 0.17256 | 0.088076 | 0.20206 | [6 empty] | 6 | 0.14385 | 0.088292 | 0.16851 | [6 empty] | 6 | 0.12962 | 0.088416 | 0.15187 |  |  | 6 | 0.1173 | 0.088535 | 0.13747 |  |  | 6 | 0.11158 | 0.088594 | 0.13078
| DR | 20.98% | [8 empty] | DR | 16.52% | [8 empty] | DR | 14.38% |  |  |  |  | DR | 12.57% |  |  |  |  | DR | 11.73%
| PPD | 10.44% | [8 empty] | PPD | 8.493% | [8 empty] | PPD | 7.629% |  |  |  |  | PPD | 6.931% |  |  |  |  | PPD | 6.621%
| ISO category | C | [8 empty] | ISO category | B | [8 empty] | ISO category | B |  |  |  |  | ISO category | B |  |  |  |  | ISO category | B
| PMV | 0.53169 | [8 empty] | PMV | 0.42348 | [8 empty] | PMV | 0.3608 |  |  |  |  | PMV | 0.29972 |  |  |  |  | PMV | 0.26865
| V'' Result | 5.9295 | [8 empty] | V'' Result | 5.9295 | [8 empty] | V'' Result | 5.9295 |  |  |  |  | V'' Result | 5.9295 |  |  |  |  | V'' Result | 5.9295
| Distance Result | 10.0593 | [8 empty] | Distance Result | 10.0593 | [8 empty] | Distance Result | 10.0593 |  |  |  |  | Distance Result | 10.0593 |  |  |  |  | Distance Result | 10.0593
| Average Dist | DN250 R1 | DN250 | DN355 R1 | DN355 | DN500 R1 | DN500 | DN710 R1 | DN710 | DN1000 R1 | DN1000 | DN1340
| Cmax | 47.1839 | 44.5488 | 19.5561 | 17.157 | 15.4514 | 14.8607 | 13.6245 | 13.4312 | 13.0267 | 12.9405 | 12.7364
| Cmin |  | 31.1549 | 7.0186 | 6.2882 | 5.7413 | 5.5467 | 5.1311 | 5.0651 | 4.9262 | 4.8965 | 4.8258
| ACCEPT | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE
| Cmax |  |  |  |  | 15.4514 | 14.8607 | 13.6245
| Cmin |  |  |  |  | 5.7413 | 5.5467 | 5.1311
| Average | 10.0593 | m
Results
|  | DN250 R1 | DN250 | DN355 R1 | DN355 | DN500 R1 | DN500 | DN710 R1 | DN710 | DN1000 R1 | DN1000 | DN1340
| Max Airflow | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
| Max Recommended Airflow | 178.5576 | 199.371 | 358.2106 | 451.3234 | 660.5534 | 779.9569 | 1331.9399 | 1572.7051 | 2642.2136 | 3119.8277 | 5601.9626
| Min Airflow | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
| Min Permissible Airflow | 59.1 | 84.4 | 118.9 | 169.6 | 234.6 | 335 | 471.8 | 672.6 | 930.7 | 1328.8 | 2385.9933
| Static Pressure | 585.9712 | 451.9026 | 145.8291 | 83.5352 | 43.7843 | 29.7875 | 10.7688 | 7.3262 | 2.7365 | 1.8617 | 0.57742
| Total Pressure | 677.4813 | 543.4126 | 168.336 | 106.042 | 49.5037 | 35.5069 | 12.1754 | 8.7329 | 3.094 | 2.2192 | 0.68829
| Max Permissible P | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
| Sound Power Level | 86.1895 | 81.5751 | 70.3388 | 61.193 | 51.333 | 45.9814 | 32.9475 | 29.0703 | 16.3667 | 12.4845 | -2.1255
| ΔT_max (heating) | 81.0065 | 56.7963 | 28.2286 | 19.836 | 10.1258 | 7.0995 | 3.5286 | 2.4795 | 1.2612 | 0.88744 | 0.36883
| Guide ring mm | 13.3 | 13.3 | 13.95 | 12.09 | 11.7 | 7.8 | -1.825 | -9.125 | -25.5 | -33.15 | -58.055
| T n.s. | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
| Hmin | 2.75 | 2.75 | 2.75 | 3.3 | 3.85 | 4.4 | 4.95 | 5.5 | 6.05 | 6.6 | 7.15
| Cmax | 47.1839 | 44.5488 | 19.5561 | 17.157 | 15.4514 | 14.8607 | 13.6245 | 13.4312 | 13.0267 | 12.9405 | 12.7364
| Cmin |  | 31.1549 | 7.0186 | 6.2882 | 5.7413 | 5.5467 | 5.1311 | 5.0651 | 4.9262 | 4.8965 | 4.8258
| Mean Air Velocity | 0.20206 | 0.19567 | 0.16851 | 0.16051 | 0.15187 | 0.14797 | 0.13747 | 0.13544 | 0.13078 | 0.1297 | 0.127
| Draft Rating | 20.98% | 20.11% | 16.52% | 15.48% | 14.38% | 13.89% | 12.57% | 12.31% | 11.73% | 11.6% | 11.26%
| PPD | 10.44% | 10.05% | 8.493% | 8.07% | 7.629% | 7.436% | 6.931% | 6.837% | 6.621% | 6.572% | 6.45%
| PMV | C | C | B | B | B | B | B | B | B | B | B
| PPD Class | 53.17% | 51.26% | 42.35% | 39.43% | 36.08% | 34.5% | 29.97% | 29.05% | 26.86% | 26.34% | 25.02%
| T s. | n.r. | n.r. | n.r. | n.r. | 30 | 26 | 23.5286 | 22 | 22 | 22 | -
|  | 209.165 | 250 | 297.0143 | 355 | 418.33 | 500 | 594.0286 | 710 | 836.66 | 1000 | 1340 |  |  | 209.165 | 250 | 297.0143 | 355 | 418.33 | 500 | 594.0286 | 710 | 836.66 | 1000
| Stroke | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
| ΔT_max (heating) | 81.0065 | 56.7963 | 28.2286 | 19.836 | 10.1258 | 7.0995 | 3.5286 | 2.4795 | 1.2612 | < +1 K | < +1 K
| Guide Ring mm | 13.3 | 13.3 | 13.95 | 12.09 | 11.7 | 7.8 | 3.5286 | 2.4795 | 1.2612 | < +1 K | < +1 K
| T n.s. | +18 | +18 | +18 | +18 | 10.1258 | 7.0995 | 3.5286 | 2.4795 | 1.2612 | < +1 | < +1
| Guide Ring mm | 13.3 | 13.3 | 13.95 | 12.09 | 11.7 | 7.8 | 3.5286 | 2.4795 | 1.2612 | < +1 | < +1
[15 empty] | 77.0065 | 52.7963 | 24.2286 | 15.836 | 6.1258 | 3.0995 | -0.47142 | -1.5205 | -2.7388 | -3.1126
1 | Result Validation | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 0
2 |  | DN250 R1 | DN250 | DN355 R1 | DN355 | DN500 R1 | DN500 | DN710 R1 | DN710 | DN1000 R1 | DN1000 | DN1340
3 | Max Airflow [L/s] | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
4 | Max Permissible Airflow [L/s] | 178.5576 | 199.371 | 358.2106 | 451.3234 | 660.5534 | 779.9569 | 1331.9399 | 1572.7051 | 2642.2136 | 3119.8277 | 5601.9626
5 | Min Airflow (Turndown To) [L/s] | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
6 | Min Permissible Airflow [L/s] | 59.1 | 84.4 | 118.9 | 169.6 | 234.6 | 335 | 471.8 | 672.6 | 930.7 | 1328.8 | 2385.9933
7 | Static Pressure | 585.9712 | 451.9026 | 145.8291 | 83.5352 | 43.7843 | 29.7875 | 10.7688 | 7.3262 | < 5 | < 5 | < 5
8 | Total Pressure | 677.4813 | 543.4126 | 168.336 | 106.042 | 49.5037 | 35.5069 | 12.1754 | < 10 | < 10 | < 10 | < 10
9 | Max Permissible P | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
10 | Sound Power Level | 86.1895 | 81.5751 | 70.3388 | 61.193 | 51.333 | 45.9814 | 32.9475 | 29.0703 | < 20 | < 20 | < 20
11 | ΔT_max (heating) | 81.0065 | 56.7963 | 28.2286 | 19.836 | 10.1258 | 7.0995 | 3.5286 | 2.4795 | 1.2612 | < +1 K | < +1 K
12 | T n.s. | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | -
13 | Cmax | - | 44.5 | 19.6 | 17.2 | 15.5 | 14.9 | 13.6 | 13.4 | 13 | 12.9 | 12.7
14 | Cmin | - | 31.2 | 7 | 6.3 | 5.7 | 5.5 | 5.1 | 5.1 | 4.9 | 4.9 | 4.8
15 | Hmin | 2.8 | 2.8 | 2.8 | 3.3 | 3.9 | 4.4 | 5 | 5.5 | 6.1 | 6.6 | 7.2
16 | Mean Air Velocity |  | 0.19567 | 0.16851 | 0.16051 | 0.15187 | 0.14797 | 0.13747 | 0.13544 | 0.13078 | 0.1297 | 0.127
17 | Draft Rating |  | 20.11% | 16.52% | 15.48% | 14.38% | 13.89% | 12.57% | 12.31% | 11.73% | 11.6% | 11.26%
18 | PPD |  | 10.05% | 8.493% | 8.07% | 7.629% | 7.436% | 6.931% | 6.837% | 6.621% | 6.572% | 6.45%
19 | PPD Class | bar: 2 to 11
20 | PMV |  | 0.5126 | 0.42348 | 0.39426 | 0.3608 | 0.34496 | 0.29972 | 0.29054 | 0.26865 | 0.26344 | 0.25019
21 | T s. | n.r. | n.r. | n.r. | n.r. | 30 | 26 | 24 | 22 | 22 | 22 | -
22 | ΔT_max (heating) | +18 | +18 | +18 | +18 | 10.1258 | 7.0995 | 3.5286 | 2.4795 | 1.2612 | < +1 | < +1
Highlighting Rules
| Max Permissible dT | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | true = manual input selected and selected heating > permissible heating (i.e. true = warning)
true = show as K
| cmax | #VALUE! | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
| cmin | #VALUE! | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
| hmin | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE
|  |  | dT heating |  |  |  |  | Model |  |  | mm (100%)
| Model Selection | 1: 6; 2: 7.0995; 7: 1; 8: DN250-R1; 9: 81.0065; 10: 13.3
[8 empty] | 2 | DN250-R0 | 56.7963 | 13.3
| Controls | 1: Left; 7: 3; 8: DN355-R1; 9: 28.2286; 10: 18.6
|  | V | T |  |  | mm |  | 4 | DN355-R0 | 19.836 | 18.6
|  | 10 | -6 |  | 0% | 26 |  | 5 | DN500-R1 | 10.1258 | 26
|  | 2 | 14.1991 |  | 100% | 0 |  | 6 | DN500-R0 | 7.0995 | 26
[8 empty] | 7 | DN710-R1 | 3.5286 | 36.5
|  | dT | V |  | % |  |  | 8 | DN710-R0 | 2.4795 | 36.5
|  | -12 | 10 |  |  |  |  | 9 | DN1000-R1 | 1.2612 | 51
|  | -6 | 10 |  | 0% | 26 |  | 10 | DN1000-R0 | 0.88744 | 51
|  | 0 | 7.6237 | 7.6 V | 29.7% | 18.2769 | mm
| Right | 1: 7.0995; 2: 2; 4: 100%; 5: 0
+ 7.1K
| Manual dT | 1: 0; 2: 0; 3: -10
Guide Ring Settings
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
| Model | DN250 R1 | DN250 | DN355 R1 | DN355 | DN500 R1 | DN500 | DN710 R1 | DN710 | DN1000 R1 | DN1000 | DN1340
|  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
|  | -8 | -8 | -8 | -8 | -8 | -8 | -8 | -8 | -8 | -8 | -8
| 2x dT | 162.013 | 113.5926 | 56.4572 | 39.6721 | 20.2516 | 14.1991 | 7.0572 | 4.959 | 2.5224 | 1.7749 | 0.73766
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Max dT | 81.0065 | 56.7963 | 28.2286 | 19.836 | 10.1258 | 7.0995 | 3.5286 | 2.4795 | 1.2612 | 0.88744 | 0.36883
| Intercept | 4.706% | 6.579% | 12.41% | 16.78% | 28.32% | 36.04% | 53.13% | 61.73% | 76.03% | 81.84% | 91.56%
|  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
| Setting | 9% | 13% | 25% | 34% | 57% | 72% | 106% | 123% | 152% | 164% | 183%
| Round <20% | 0% | 0% | 25% | 34% | 57% | 72% | 106% | 123% | 152% | 164% | 183%
| Inverse | 1 | 1 | 0.75 | 0.66 | 0.43 | 0.28 | -0.06 | -0.23 | -0.52 | -0.64 | -83%
| Round | 100% | 100% | 75% | 65% | 45% | 30% | -5% | -25% | -50% | -65% | -85%
|  | 13.3 | 13.3 | 18.6 | 18.6 | 26 | 26 | 36.5 | 36.5 | 51 | 51 | 68.3
| Distance | 13.3 | 13.3 | 13.95 | 12.276 | 11.18 | 7.28 | -2.19 | -8.395 | -26.52 | -32.64 | -56.689
| Distance not rounded | 13.3 | 13.3 | 13.95 | 12.09 | 11.7 | 7.8 | -1.825 | -9.125 | -25.5 | -33.15 | -58.055
Is Min C > Max C
| Max C | - | 44.5 | 19.6 | 17.2 | 15.5 | 14.9 | 13.6 | 13.4 | 13 | 12.9 | 12.7
| Min C | - | 31.2 | 7 | 6.3 | 5.7 | 5.5 | 5.1 | 5.1 | 4.9 | 4.9 | 4.8
| Min>Max? | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Charts (hidden)
250
355
500
710
1000
DN500-R0 Electric Control Voltage (V) & Guide Ring Position (mm)
DN500-R0 Electric Control Voltage (V) & Guide Ring Position (mm)
DN500-R0 Electric Control Voltage (V) & Guide Ring Position (mm)
DN500-R0 Electric Control Voltage (V) & Guide Ring Position (mm)
DN500-R0 Electric Control Voltage (V) & Guide Ring Position (mm)

## Notes & Drawings
SMARTEMP PRODUCT SELECTION CALCULATOR
Adjustable Helical Swirl Diffuser [HSC-AD] Notes
Ceiling Type
Diffuser can be installed substantially flush with a false ceiling or freely suspended.
Acoustics
Without acoustic lining, the sound power level of the connection box is up to 2 dB(A) higher.
Diffuser Dimensions
Model | D2 | D4 | E | D5 | L | H1 | H2 | H3 | F | - note: dimensions currently not available
DN355 | 395 | 530 | 445, 595, 603 | 354 | 495 | 550 | 20 | 80 | 320 | * all dimensions in mm
DN = 355 | D2 = 395 | D4 = 530 | E = 445, 595, 603 | D5 = 354 | L = 495 | H1 = 550 | H2 = 20 | H3 = 80 | F = 320
> 355(1×DN) | 355
D4 = Ø530 OR E = □445, 595, 603
Adjustment Type Description (for 'Product Code Generator')
Symbol | Description
M | Manual adjustment only.
BE1 | DN250-DN500: With base module and electric actuator 24V, 2-10V.
BE2 | DN250-DN500: With base module and electric actuator 24V, 3-pt (2-position).
BT__ | DN250-DN500: With base module and thermal actuator set to __ (22°C/26°C/30°C, default 26°C).
E3 | DN710: With electric actuator 24V, 2-10V.
T__ | DN710: With thermal actuator set to __ (22°C/26°C/30°C, default 26°C). AVAILABLE IN 2018.
> 355(1×DN)
H2 = 20
DN = 355
D2 = 395
D4 = Ø530 OR E = □445, 595, 603
D5 = 354
H1 = 550
F = 320
H3 = 80
L = 495

## HSC-AD data diagrams (hidden)
250
355
500
710
1000
Chart Title | DN500-R0 Electric Control Voltage (V) & Guide Ring Position (mm)
DN500-R0 Electric Control Voltage (V) & Guide Ring Position (mm)
DN500-R0 Electric Control Voltage (V) & Guide Ring Position (mm)
DN500-R0 Electric Control Voltage (V) & Guide Ring Position (mm)
DN500-R0 Electric Control Voltage (V) & Guide Ring Position (mm)
DN500-R0 Electric Control Voltage (V) & Guide Ring Position (mm)
Horizontal Discharge
Vertical Discharge
Horizontal Discharge
Vertical Discharge
Horizontal Discharge
Vertical Discharge
Horizontal Discharge
Vertical Discharge
Horizontal Discharge
Vertical Discharge

## HSC-AD data (hidden)
| 95% | 0.2
| 90% | 0.25
| 80% | 0.29
| 70% | 0.33
Product code
|  |  | DN | R
|  | 1 | 250 | 1
|  | 2 | 250 | 0
|  | 3 | 355 | 1
|  | 4 | 355 | 0
|  | 5 | 500 | 1
|  | 6 | 500 | 0
|  | 7 | 710 | 1
|  | 8 | 710 | 0
|  | 9 | 1000 | 1 |  |  | - option not available for size DN710 and DN1000
|  | 10 | 1000 | 0 |  |  | - option not available for DN250 - DN500
| Model | 6 | 500 | 0 |  | warning
| Mode Code | DN500-R0
Adjustment
0
|  | 1 | M | M | Manual adjustment | Manual
|  | 2 | Electric motor 2-10V | E1 | Electric actuator 24V, 2-10V | Electric
|  | 3 | Electric motor 2-position | E2 | Electric actuator 24V, 3-pt (2 position) | Electric
|  | 4 | Thermal actuator set to 26°C | T26 | Thermal actuator set to 26°C | Thermal element
|  | 1 | M | 26 | Manual adjustment
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7
| Face Size | 250 | C375 | S345 | custom | N/A | N/A | 375
|  | 355 | C530 | S445 | S595 | S603 | custom | 530
|  | 500 | C750 | S595 | S603 | custom | N/A | 750
|  | 710 | C1000 | custom | N/A | N/A | N/A | 1000
|  | 1000 | C1420 | custom | N/A | N/A | N/A | 1420
|  |  | 1 | 2 | 3 | 4 | 5
|  | Table | C750 | S595 | S603 | custom | N/A
SELECTION
|  | 1 | C750
|  | size | 750
|  | Shape | C | mm diameter circular face
|  | Description | 750 mm diameter circular face
|  | Selection Code | C750
| Colour | 1 | RAL9003 | RAL9003 (signal white)
|  | 2 | RAL9005 | RAL9005 (jet black)
|  | 3 | <colour> | custom colour
|  | 1 | RAL9003
| Code |  | SMARTEMP HSC-AD-DN500-R0-C750-M-RAL9003
| Size |  | D2 | D4 | E | D5 | L | H1 | H2 | H3 | F
| 1 | DN250 | 270 | 375 | 295 | 249 | 425 | 400 | 14 | 60 | 215 | 250
| 2 | DN355 | 395 | 530 | 445, 595, 603 | 354 | 495 | 550 | 20 | 80 | 320 | 355
| 3 | DN500 | 560 | 750 | 595, 603 | 499 | 695 | 690 | 28 | 100 | 465 | 500
| 4 | DN710 | 790 | 1000 | [7 empty] | 710
| 5 | DN1000 |  | 1420 | [7 empty] | 1000
description
| Size | Diffuser HSC-AD-DN500-R0 (neck diameter 500 mm without reducer) | without reducer
750 mm diameter circular face
Manual adjustment
| Colour | Powder coated to RAL9003 (signal white)
summary
| Size and R | DN500-R0 | Format
2 | Max Airflow [L/s] | 600 | 600
3 | Max Permissible Airflow [L/s] | 779.9569 | 780
4 | Min Airflow (Turndown To) [L/s] | 600 | 600
5 | Min Permissible Airflow [L/s] | 335 | 335
6 | Static Pressure | 29.7875 | 29.8
7 | Total Pressure | 35.5069
8 | Max Permissible P | 60
9 | Sound Power Level | 45.9814 | 46
10 | ΔT_max (heating) | 7.0995 | 7.1 | max heating | 7.0995 | 7.1
11 | T n.s. | 16 |  | guide ring | 7.8 | 8
12 | Cmax | 14.9 | 14.9
13 | Cmin | 5.5 | 5.5
14 | Hmin | 4.4 | 4.4
15 | Mean Air Velocity | 0.14797 | 0.15
16 | Draft Rating | 0.13887 | 13.9
17 | PPD | 0.074358 | 0.074
18 | PPD Class | B
19 | PMV | 0.34496 | 0.34
20 | T s. | 26 | 26
| dT | -12
| Selected C | 10.0593
| Spec. airflow | 5.9 | L/s/m²
| input diffuser height | 6
| room temp | 23
| selected heating dt | 4
| Selected Airflow | 600 L/s @ 29.8 Pa static
| Min Permissible Airflow | 335 L/s @ ΔT = -12 K
| Max Heating | + 7.1 K
| Thermal element setting | T26
| Guide Ring | 8
Adjustment
| Manual mode | Manual Adjustment selected
8 mm recessed from face
for heating at ΔT = +4 K
| Selection | Manual Adjustment selected
| Sound Power level | 46 dB(A)
Diagram
Min Recommended Diffuser Height = 4.4 m
Selected Diffuser Height = 6 m
| Cmin | Cmax
| 5.5 | 14.9
C Max = 14.9 m
C Min = 5.5 m
Average
C select | 10.1
Average C = 10.1 m
Top box | C Max = 14.9 m | 1 | Specific Airflow Rate @ Average C = 10.1 m: 5.9 L/s/m²
box 2 | C Min = 5.5 m | 2 | Specific Airflow Rate @ Selected C = 10.1 m: 5.9 L/s/m²
box 3 | Average C = 10.1 m | 3 | Selected Specific Airflow Rate: 5.9 L/s/m²
room box | Specific Airflow Rate @ Average C = 10.1 m: 5.9 L/s/m²
Comfort Performance
ADPI | > 90%
Mean Room Air Velocity | 0.15 m/s
Mean Draught Rating @ 23 °C | 13.9% @ room temp. of 23ºC
Mean PPD | < 7.4 %
Satisfies PPD (ISO7730) | Category B
Mean PMV ^ | 0.34
adjustment | M

## Print Summary
HSC-AD Performance Calculator Summary
Project | <Project Name>
Company | <Name>
Consultant | <Name>
Product | SMARTEMP HSC-AD
Adjustable Helical Swirl Diffuser
Size | DN500-R0
Guide Ring Adjustment Type | Manual adjustment
Project Summary |  | Direction Adjustment
Selected Airflow Rate | 600 L/s @ 29.8 Pa static | Manual Adjustment selected
Min Permissible Airflow | 335 L/s @ ΔT = -12 K
Max Heating ΔT | + 7.1 K
Acoustic Performance
Sound Power Level | 46 dB(A)
Comfort Performance & Recommended Layout
ADPI | > 90%
Mean Room Air Velocity | 0.15 m/s
Mean Draught Rating | 13.9% @ room temp. of 23ºC
Mean PPD | < 7.4 %
Satisfies PPD (ISO7730) | Category B
Mean PMV * | 0.34
* ISO7730; ASHRAE Std 55
Description | Diffuser HSC-AD-DN500-R0 (neck diameter 500 mm without reducer)
750 mm diameter circular face
Manual adjustment
Powder coated to RAL9003 (signal white)
Order Code | SMARTEMP HSC-AD-DN500-R0-C750-M-RAL9003
C Max = 14.9 m
C Min = 5.5 m
Average C = 10.1 m
Min Recommended Diffuser Height = 4.4 m
Specific Airflow Rate @ Average C = 10.1 m: 5.9 L/s/m²
C2
Selected Diffuser Height = 6 m

## Tender Text (hidden)
Furnish and install SMARTEMP® Adjustable Helical Swirl Diffusers, type HSC-AD, to provide diffuse airflow with adjustable horizontal-to-vertical discharge direction for high thermal comfort from elevated discharge heights. Each diffuser is to be made of powder coated steel and shall include 20 off-set radial vanes flush with the horizontal diffuser face. The diffuser face is to be square (up to neck size DN500 only) or circular, as specified. The diffuser is to be installed substantially flush
with the suspended false ceiling or freely suspended, as specified.
Swirl vanes are to include cambered leading edges for reduced noise and pressure drop, and the helical swirl vane tips are each to incorporate a geometric twist for increased downward discharge penetration and reduced minimum airflow rates. An internal adjustable guide ring with 20 geometrically twisted guide vanes is to provide constant pressure discharge direction adjustment.
The guide ring is to be adjusted manually, electrically or thermally, as specified and in accordance with SMARTEMP guidelines. The latter two each attach as a kit to an included control module, which is optionally available for manual adjustment. Diffuser neck size is to be DN250, DN355, DN500 or DN710, as required. The diffuser is to incorporate the optional reducer and reduced guide ring, where appropriate. Diffuser discharge height of 2.5 to 15 m to be inaccordance with SMARTEMP's recommendations for the duty required.
Cooling with horizontal discharge direction to be at no less than ΔTsupply-room = -13 K. For heating applications, provide downward discharge and control maximum ΔTsupply-room no t to exceed the maximum per missible heating temperature differential prescribed by SMARTEMP for the selected diffuser, airflow rate and discharge height.
Where specified, each diffuser is to be connected to a side-entry sheet-metal connections box, internally insulated where indicated, fabricated in accordance with SMARTEMP's recommendations. Alternatively, each diffuser is to be connected to a vertical duct of internal diameter equal to the diffuser DN size and at least one duct diameter in length.